## PRICE SCHEDULE

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| **Item No.** | **Brief Description of Goods** | **Explanatory Note** | **Quantity** | **Unit Price****(GYD)** | **Delivery Cost plus taxes** | **Total Cost (GYD)** |
|  **1** | ***Supply and Delivery of Six (6) Electric Vehicle Charging Stations***  | **Electric Vehicle Charging Station**:1. Charge mode: Level 3 DC Fast Charging Station
2. Output power: 22kW - 25kW
3. Connectors: Dual port (1 x CHAdeMO and 1 x CCS2) - fully sealed
4. Input voltage: 3-phase, 277/480Vac ±10%, 60Hz OR 230/400 Vac ±10%, 60Hz
5. Output voltage range: 200 – 500Vdc (CCS2) and 50 – 500Vdc (CHAdeMO)
6. Protection: overload, ground fault, overvoltage, output overcurrent, output short-circuit protection, temperature rise, surge protection
7. Installation method: Floor stand with pedestal and Wall mount
8. Charge cable length: ≥ 18"/5.5m
9. Features: RFID card reader for user authentication or QR or NFC (ISO 14443)
10. Network connectivity: OCPP compliant
11. Communication Protocol: OCPP 1.5 S / 1.6 J
12. Protection: UL 50E - 3R, IEC 60529, IP 54 - IK 10 vandal-proof casing
13. Certification: UL 2202, UL 2231, UL 2594, RoHS, IEEE 519 or any other equivalent certification
14. Display screen: OLED/ LCD IPS – full colour
15. Connectivity: Wi-fi/3G/4G, Ethernet
16. Warranty: 3 years
 | 6 |  |  |  |

**Please note that the procuring entity will not be responsible for customs clearance of the goods. Goods and services purchased using donor funds are zero rated however ,only imported goods and services are zero rated when purchased using government funds.**

Duly authorized to sign for and on behalf of

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

(*name of Bidder*)

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ \_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ (*Full name) (Title) (Signature and seal)*

27